{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":39,"n_cols":7,"rows_kept":39,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","5XXM-A"]
[]
[]
[]
[]
["","","","","","5XXM68A2V1B","5XXM90A2V1B"]
["Dimenzije","Uređaj","","Visina","mm","734","734"]
["","","","Širina","mm","1040","1040"]
["","","","Dubina","mm","408","408"]
["Težina","Uređaj","","","kg","69.0","73.0"]
["Kompresor","Tip","","","","Hermetički zabrtvljen kompresor s klatnom","Hermetički zabrtvljen kompresor s klatnom"]
["Raspon rada","Hlađenje","Ambijent:","Min.","°CDB","-10","-10"]
["","","","Maks.","°CDB","50","50"]
["Razina tlaka zvuka","Hlađenje","","Nom.","dBA","48.0 (2)","52.0 (2)"]
["","Grijanje","","Nom.","dBA","49.0 (2), 51.0 (3)","53.0 (2), 55.0 (3)"]
["Radna tvar","Tip","","","","R-32","R-32"]
["","Punjenje","","","kg","2.00","2.40"]
["","Punjenje","","","tCO2Eq","1.35","1.62"]
["","GWP","","","","675","675.0"]
["Priključci cjevovoda ","Duljina cjevovoda ","Maks. ","OU - IU","m","25 (4) (5)","25 (5) (4)"]
["Priključci cjevovoda","Punjenje dodatne radne tvari","","","kg/m","0,02 (za duljinu cjevovoda koja premašuje 30 m)","0,02 (za duljinu cjevovoda koja premašuje 30 m)"]
["","Razlika razine","IU - OU","Maks.","m","15.0 (5)","15.0 (5)"]
["","","IU - IU","Maks.","m","7.5 (5)","7.5 (5)"]
["","Ukupna duljina cjevovoda","Sustav","Stvarno","m","60","75"]
["Standardna dodatna oprema","Priručnik za instalaciju","","","","1","1"]
["","Drenažni poklopac","","","","3","3"]
["","Drenažni čep","","","","1","1"]
["","Sklop reduktora","","","","1","1"]
["","Vreća s vijcima","","","","2","2"]
["Raspon energetske učinkovitosti","","","","","A+++ ~ D","A+++ ~ D"]
["Napajanje","Faza","","","","1~","1~"]
["","Frekvencija","","","Hz","50","50"]
["","Napon","","","V","220-240","220-240"]
["Napomene","","","","","(1) - Pogledajte odvojene nacrte za radno područje","(1) - Pogledajte odvojene nacrte za radno područje"]
["","","","","","(2) - For DX combination","(2) - For DX combination"]
["","","","","","(3) - For Space heating operation of CHVX07 unit","(3) - For Space heating operation of CHVX07 unit"]
["","","","","","(4) - Za jednu prostoriju","(4) - Za jednu prostoriju"]
["","","","","","(5) - For combination with FBA71/100/125 refer to installation manual","(5) - For combination with FBA71/100/125 refer to installation manual"]
["","","","","","(6) - Sadrži fluorovodične stakleničke plinove","(6) - Sadrži fluorovodične stakleničke plinove"]